## DC Load
DC Load Calculation
DC Device | Number of Devices | Load (Watts) | Hours of Use/day | Daily Watt-hours
With TBA30xx PMU
5W TB8100 base - Tx, 5W | 0 | 32 | 0 | 0
50W TB8100 base - Tx, 50W | 1 | 125 | 4 | 500
100W TB8100 base - Tx, 100W | 0 | 240 | 0 | 0
TB8100 Rx, normal mode | 1 | 12.5 | 20 | 250
TB8100 Rx, 20ms Rx/Tx cycling | 0 | 9.3 | 0 | 0
TB8100 Rx, sleep mode, 200mS cycling | 0 | 5 | 0 | 0
TB8100 Rx, Deep sleep, 200ms cycling | 0 | 2 | 0 | 0
TB8100 Rx, Deep sleep, 500ms cycling | 0 | 1.52 | 0 | 0
TB8100 Rx, Deep sleep, 1sec cycling | 0 | 1.36 | 0 | 0
TB8100 Rx, Deep sleep, 5sec cycling | 0 | 1.23 | 0 | 0
With 12 V DC PA
5W TB8100 base - Tx, 5W | 0 | 25 | 0 | 0
50W TB8100 base - Tx, 50W | 0 | 107 | 0 | 0
TB8100 Rx, normal mode | 0 | 8.8 | 0 | 0
TB8100 Rx, 20ms Rx/Tx cycling | 0 | 7.2 | 0 | 0
TB8100 Rx, sleep mode, 200mS cycling | 0 | 4.3 | 0 | 0
TB8100 Rx, Deep sleep, 200ms cycling | 0 | 1.5 | 0 | 0
TB8100 Rx, Deep sleep, 500ms cycling | 0 | 1.02 | 0 | 0
TB8100 Rx, Deep sleep, 1sec cycling | 0 | 0.87 | 0 | 0
TB8100 Rx, Deep sleep, 5sec cycling | 0 | 0.75 | 0 | 0
spare | 0 | 0 | 0 | 0
spare | 0 | 0 | 0 | 0
spare | 0 | 0 | 0 | 0
spare | 0 | 0 | 0 | 0
DC load in watt-hours/day |  |  |  | 750
(automatically forwarded to Solar Array Sizing Sheet)
Note: |  | = Data Entry

## AC Load
AC Load Calculation
AC Device | Number of Devices | Load (Watts) | Hours of Use/day | Daily Watt-hours
5W TB8100 base - Tx, 5W | 0 | 41 | 0 | 0
50W TB8100 base - Tx, 50W | 0 | 132 | 0 | 0
100W TB8100 base - Tx, 100W | 0 | 230 | 0 | 0
TB8100 Rx, normal mode, Single Rack | 0 | 19 | 0 | 0
TB8100 Rx, normal mode, Dual Rack | 0 | 33 | 0 | 0
spare | 0 | 0 | 0 | 0
spare | 0 | 0 | 0 | 0
spare | 0 | 0 | 0 | 0
spare | 0 | 0 | 0 | 0
spare | 0 | 0 | 0 | 0
Total daily AC load |  |  |  | 0
Factor for inverter efficiency |  |  |  | 0.86
AC load expressed as DC |  |  |  | 0
(automatically forwarded to Solar Array Sizing Sheet)
Note: |  | = Data Entry

## Solar Array Sizing
Solar Array Sizing Procedure
DC load in watt-hours/day | 750 | W/hrs
AC load expressed as DC | 0 | W/hrs
Total load | 750 | W/hrs
System nominal DC voltage | 12 | Volts
Total load in ampere-hours (Line 4/Line 5) | 62.5 | Ah
System losses/safety factor multiplier | 1.2
Adjusted total daily load (line 6 X line 7) | 75 | Ah
Worst month daily average insolation (from map) | 4.5 | ESH
Required array current (Line 8/Line 9) | 16.6667 | Amps
Current at maximum power (Impp) of selected module | 4.7619 | Amps
Number of parallel modules required | 3.5
Line 12 rounded up to next whole number | 4
Number of series modules required | 1
Total modules in array (Line 13 X Line 14) | 4
Solar Panel Calculator
(Tip: Enter 2 values to get a 3rd, unknown, value)
Enter solar panel peak rated watts @ 25 deg. C | 80 | Watts | 0 | Watts
Enter solar panel peak rated voltage @ mpp-Volts | 16.8 | Volts | 0 | Volts
Enter solar panel peak rated current @ mpp-Current | 0 | Amps | 4.7619 | Amps
Note: |  | = Data Entry

## Battery Sizing
Estimating Required Battery Capacity
| Latitude | Days of Reserve
| 0 - 30 | 5 - 6
| 30 - 50 | 10 - 12
| 50 - 60 | 15
Selected days of reserve | 4
Adjustment for cycling capacity (insert 0.8 for deep-cycle, 0.5 for shallow) | 0.5
Adjusted total daily load | 75 | ampere-hours
Recommended nominal battery capacity | 600 | Ah at | 12 | volts or | 7.2 | kWh
Note: |  | = Data Entry